Dell VRTX rack conversion (The JDN way)

Introduction	1

Required tools	1

Disclaimer	1

Conversion	2

# Introduction

The rack conversion procedure proposed by Dell is overly complicated and time consuming. As a work around, we propose the following procedure instead.

# Required tools

The required tools to complete this task are

- #1 Phillips screwdriver

- Torx wrench provided with the Rack conversion kit

# Disclaimer

The location of the JDN number is not correct in the following pictures! Please use the VRTX assembly manual to find out where to place JDN number.

# Conversion

- Remove the VRTX top cover

- Remove the black screw at the rear left side of the VRTX (next to the blower under the CMC)

- Pull back the blue clip and flip out the left side PCI door

- Remove the left side lower panel by sliding it to the rear of the VRTX

- Take the left side PCI door (removed in step 3) and remove the plastic finish of the metal frame by unscrewing the screws

Before													  After

- Fill the PCI door gab in the VRTX frame by mounting the blocking plate which was created in the previous step. The blocking plate should click when mounted properly

- Remove the right side rear screw which is holding the right side VRTX cover

- Remove the right side finish as shown in the picture below

- Remove the screws which are holding the left rack ear at the front in place

- Carefully remove the rack ear and take out the 2 torx screws which are holding the blocking plate in place. Be gentle, the cable to the display cannot be disconnected!

- Insert the correct piece of the VRTX rack mount kit in the gab of the removed blocking plate

- Mount the rack ear back to the chassis

- Repeat steps 9 to 12 for the right side rack ear

When all steps are followed as described in this manual, the VRTX should be ready for rack mounting.